# HVAC System Operations & Maintenance Manual

## 1. Introduction

### 1.1 Purpose

This manual provides comprehensive guidance for the operation, maintenance, and troubleshooting of the HVAC system installed at [Facility Name]. It serves as the primary reference for facility engineers, technicians, and operators.

### 1.2 System Description

Building Type: Commercial Office Building Total Area: 50,000 sq ft Zones: 4 primary zones (North, South, East, West) Operating Hours: 6:00 AM - 8:00 PM (Mon-Fri)

## 2. Equipment Specifications

### 2.1 Air Handling Units (AHUs)

- Manufacturer: Carrier

- Model: 39M

- Quantity: 4 units

- Capacity: 20,000 CFM each

- Motor: 25 HP, 460V, 3-phase

- Filter Types:

  - Pre-filter: MERV 8

  - Final filter: MERV 13

- Design Parameters:

  - Supply Air Temp: 55°F ± 2°F

  - Return Air Temp: 75°F ± 2°F

  - Static Pressure: 2.5“ WC

### 2.2 Chillers

- Manufacturer: Trane

- Model: CVHF

- Type: Water-cooled centrifugal

- Capacity: 500 tons

- Refrigerant: R-134a

- Operating Parameters:

  - Chilled Water Supply: 44°F

  - Chilled Water Return: 54°F

  - Condenser Water Supply: 85°F

  - Condenser Water Return: 95°F

  - Minimum Flow: 600 GPM

  - Maximum Flow: 1200 GPM

### 2.3 Cooling Towers

- Manufacturer: Baltimore Aircoil

- Model: Series 3000

- Type: Induced draft counterflow

- Capacity: 600 tons

- Fan Motor: 30 HP

- Design Conditions:

  - Wet Bulb: 78°F

  - Range: 10°F

  - Approach: 7°F

### 2.4 Boilers

- Manufacturer: Cleaver-Brooks

- Model: CFC-E

- Type: Fire-tube condensing

- Input: 4,000 MBH

- Output: 3,800 MBH

- Efficiency: 95%

- Fuel: Natural Gas

- Operating Parameters:

  - Supply Temperature: 180°F

  - Return Temperature: 160°F

  - Operating Pressure: 30 PSI

## 3. Safety Procedures

### 3.1 Required Personal Protective Equipment (PPE)

- Safety glasses (ANSI Z87.1)

- Steel-toed boots (ASTM F2413-18)

- Hard hat (Type I, Class E)

- Hearing protection (NRR 25+)

- Chemical-resistant gloves (when handling water treatment chemicals)

- Respirator (when handling refrigerants)

### 3.2 Lockout/Tagout Procedures

- Notify affected personnel

- Shut down equipment

- Isolate energy sources:

  - Electrical disconnects

  - Mechanical valves

  - Pneumatic systems

- Apply locks and tags

- Verify zero energy state

- Complete lockout log

### 3.3 Confined Space Entry

Requirements for entering confined spaces (cooling towers, tanks):

- Entry permit

- Gas monitor calibration

- Ventilation equipment

- Safety harness and lifeline

- Attendant present

- Emergency rescue plan

## 4. Operating Procedures

### 4.1 Daily Start-up Sequence

- System Check (5:00 AM)

  - Verify BMS operation

  - Check equipment status

  - Review alarms

- Cooling Tower Start (5:15 AM)

  - Open isolation valves

  - Start condenser water pumps

  - Verify water flow

  - Enable fan operation

- Chiller Operation (5:30 AM)

  - Verify oil temperature

  - Check refrigerant levels

  - Enable chiller controls

  - Monitor approach temperatures

- Air Handler Start (5:45 AM)

  - Open outdoor air dampers

  - Start supply/return fans

  - Enable temperature controls

  - Verify proper pressurization

### 4.2 Normal Operation Monitoring

Hourly Checks:

- Supply air temperature: 55°F ± 2°F

- Return air temperature: 75°F ± 2°F

- Chilled water supply: 44°F ± 1°F

- Condenser water return: 95°F maximum

- Zone temperatures: 72°F ± 2°F

- Static pressure: 2.5“ WC ± 0.2“

### 4.3 Shutdown Procedure

- Reduce cooling load

- Disable AHUs sequentially

- Shut down chillers per manufacturer protocol

- Continue condenser water flow for 5 minutes

- Shut down cooling tower fans

- Close isolation valves

- Document readings

## 5. Maintenance Procedures

### 5.1 Daily Tasks

- Log operating parameters

- Check equipment for unusual noise/vibration

- Inspect for leaks

- Monitor differential pressures

- Record energy consumption

- Check zone temperatures

- Verify proper drainage

### 5.2 Weekly Tasks

Cooling Tower:

- Clean strainers

- Check water chemistry

- Inspect fill material

- Verify fan operation

- Test water treatment system

Chillers:

- Check oil level/pressure

- Record operating temperatures

- Inspect for refrigerant leaks

- Clean local control panels

- Verify safety controls

AHUs:

- Check belt tension

- Inspect filter condition

- Clean drain pans

- Verify damper operation

- Test safety controls

### 5.3 Monthly Tasks

- Lubricate all bearings

- Replace air filters

- Clean cooling tower fill

- Test water quality

- Calibrate sensors

- Check electrical connections

- Test emergency systems

- Clean strainers

- Inspect insulation

- Check valve operation

### 5.4 Quarterly Tasks

- Clean cooling tower

- Test refrigerant levels

- Analyze oil samples

- Clean heat exchangers

- Test safety controls

- Calibrate BMS sensors

- Check VFD operation

- Service pump seals

- Inspect ductwork

- Clean coils

### 5.5 Annual Tasks

- Clean condenser tubes

- Clean evaporator tubes

- Replace oil filters

- Test relief valves

- Major electrical inspection

- Thermographic scanning

- Vibration analysis

- Cooling tower overhaul

- Boiler inspection

- Air balance verification

## 6. Troubleshooting Guide

### 6.1 Chiller Issues

#### High Condenser Pressure

Symptoms:

- High head pressure

- High approach temperature

- Reduced capacity

Possible Causes:

- Dirty condenser tubes

- Non-condensables in system

- Cooling tower malfunction

- Excessive refrigerant charge

Solutions:

- Clean condenser tubes

- Purge non-condensables

- Check cooling tower operation

- Verify refrigerant charge

#### Low Suction Pressure

Symptoms:

- Low evaporator temperature

- Reduced cooling capacity

- Possible freezing

Possible Causes:

- Low refrigerant charge

- Dirty evaporator

- Low water flow

- Failed expansion valve

Solutions:

- Check refrigerant charge

- Clean evaporator tubes

- Verify pump operation

- Inspect/replace expansion valve

### 6.2 AHU Issues

#### Insufficient Cooling

Symptoms:

- High space temperature

- High supply air temperature

- Low ΔT across coil

Possible Causes:

- Low chilled water flow

- Air in system

- Dirty cooling coil

- Control valve failure

Solutions:

- Check pump operation

- Vent air from system

- Clean cooling coil

- Repair/replace valve

#### Fan Vibration

Symptoms:

- Excessive noise

- Visible movement

- High vibration readings

Possible Causes:

- Unbalanced fan

- Worn bearings

- Loose mounting

- Belt issues

Solutions:

- Balance fan assembly

- Replace bearings

- Tighten mounting

- Replace/align belts

## 7. Emergency Procedures

### 7.1 Refrigerant Leak

Immediate Actions:

- Evacuate area

- Ventilate space

- Don PPE

- Shut down system

- Isolate leak

- Contact service provider

Recovery Steps:

- Assess leak severity

- Repair leak

- Pressure test system

- Recharge refrigerant

- Test operation

- Document incident

### 7.2 Water Leak

Immediate Actions:

- Identify source

- Shut off water supply

- Power down equipment

- Contain spread

- Remove standing water

- Document damage

Recovery Steps:

- Repair leak

- Dry affected areas

- Test systems

- Restore operation

- Monitor for issues

- Update procedures

### 7.3 Power Failure

Immediate Actions:

- Check backup power

- Secure equipment

- Close outside air dampers

- Monitor temperatures

- Notify occupants

- Contact utility

Recovery Steps:

- Verify power quality

- Reset equipment

- Sequential start-up

- Check operation

- Document event

- Review procedures

## 8. Documentation & Records

### 8.1 Required Logs

Daily Operating Log:

- Equipment run times

- Temperature readings

- Pressure readings

- Energy consumption

- Alarm conditions

- Operator notes

Maintenance Log:

- Completed tasks

- Parts replaced

- Contractor visits

- Test results

- Calibration data

- Repair history

### 8.2 Equipment History

For each major component:

- Installation date

- Warranty information

- Maintenance history

- Repair records

- Modification details

- Performance data

### 8.3 Compliance Records

- Refrigerant usage

- Water treatment

- Safety inspections

- Training records

- Permits/certifications

- Environmental reports

## 9. Essential Contacts

### 9.1 Emergency Contacts

- Fire Department: [Number]

- Police: [Number]

- Ambulance: [Number]

- Poison Control: [Number]

- Building Security: [Number]

### 9.2 Service Providers

- HVAC Contractor: [Company Name, Number]

- Controls Contractor: [Company Name, Number]

- Water Treatment: [Company Name, Number]

- Electrical Contractor: [Company Name, Number]

- Equipment Manufacturer: [Company Name, Number]

### 9.3 Utility Contacts

- Electric Utility: [Company Name, Number]

- Gas Utility: [Company Name, Number]

- Water Utility: [Company Name, Number]

## 10. Appendices

### 10.1 Technical Specifications

- Equipment submittal data

- Performance curves

- Control sequences

- Design drawings

- Test reports

### 10.2 Forms and Checklists

- Daily inspection form

- Maintenance checklist

- Safety inspection form

- Lockout/tagout permits

- Incident reports

### 10.3 Reference Documents

- Original equipment manuals

- Control system manual

- As-built drawings

- Warranty documents

- Training materials

Last Updated: December 27, 2024 Version: 2.0 Document Owner: [Facility Manager Name]